LIGHTNING DETECTION SYSTEM

Technical Data Sheet

____________________________________________________________

Reference Document

# TABLE OF CONTENTS

1.  Product Overview

2.  System Performance Specifications

3.  Detection Capabilities

4.  Data Output and Communication

5.  Alert and Notification Features

6.  Power System Specifications

7.  Environmental Ratings

8.  Mechanical Specifications

9.  Installation Requirements

10. Maintenance Schedule

11. Performance Comparison

12. Limitations and Disclaimers

13. Ordering and Support

# 1. Product Overview

## 1.1 Description

This standalone, solar-powered lightning detection system is designed for deployment at a wide range of outdoor sites including industrial facilities, weather stations, agricultural operations, and remote installations. The system provides continuous, autonomous lightning monitoring with real-time cloud data publishing, proximity-based alert notifications, and comprehensive local data logging.

The system is engineered for reliable operation in demanding environments where conventional lightning detection equipment may experience excessive false triggers due to electromagnetic interference (EMI) from surrounding equipment and infrastructure.

## 1.2 Key Features

Continuous 24/7 lightning detection up to 40 km range

Storm distance estimation with 14-level resolution

Lightning energy measurement for each detected event

Cloud-to-ground and intra-cloud lightning detection

Configurable EMI rejection for demanding environments

Solar-powered with lithium-ion battery backup

Real-time cloud data publishing via HTTPS (TLS 1.2+)

Configurable proximity alerts (SMS, WhatsApp, Email)

Automated weekly summary reports with PDF attachment

Local CSV data logging with daily file rotation

IP65+ weatherproof enclosure (IP67 available)

Mast-mount or pole-mount installation

Non-metallic enclosure for optimal RF transparency

NTP time synchronisation for accurate event timestamps

Offline data buffering with automatic cloud sync on reconnect

Wi-Fi signal strength monitoring

## 1.3 Typical Applications

Industrial plants and foundries

Mining and quarrying operations

Weather monitoring stations

Agricultural and farming operations

Airport and aviation weather observation

Outdoor event safety management

Construction site safety

Power utility and transmission line monitoring

Telecommunications tower monitoring

Sports and recreation facility weather safety

Solar and wind farm installations

Oil and gas facilities

# 2. System Performance Specifications

## 2.1 Detection Performance

| Parameter | Specification |
| --- | --- |
| Maximum Detection Range | 40 km |
| Distance Estimation Levels | 14 discrete levels + out of range |
| Distance Reporting Values | 1, 5, 6, 8, 10, 12, 14, 17, 20, 24, 27, 31, 34, 37, 40 km |
| Distance Estimation Accuracy | +/- 4 km (manufacturer rated) |
| Detection Types | Cloud-to-ground, intra-cloud |
| Lightning Energy | 21-bit relative measurement per event |
| Antenna Frequency | 500 kHz (+/- 3.5%) |
| Disturber Rejection | Hardware-embedded algorithm |
| Noise Floor | 7 programmable levels (0-7) |
| Watchdog Threshold | Configurable (10 levels) |
| Spike Rejection | Configurable (12 levels) |
| Minimum Strike Threshold | 1, 5, 9, or 16 events |
| Event Latency (detect to log) | < 2 seconds typical |

## 2.2 System Performance

| Parameter | Specification |
| --- | --- |
| Heartbeat Interval | 120 seconds (configurable) |
| Cloud Publish Latency | < 2 seconds from detection |
| Local Log Format | CSV (daily rotation) |
| Time Accuracy | NTP synchronised (UTC) |
| Wi-Fi Connectivity | 2.4 GHz 802.11 b/g/n |
| Cloud Protocol | HTTPS POST (TLS 1.2+) |
| Offline Buffering | Automatic local buffer, sync on reconnect |
| Alert Response Time | < 5 seconds from detection |
| Weekly Report Generation | Automated PDF + email delivery |

# 3. Detection Capabilities

## 3.1 Lightning Detection Technology

The system utilises an industry-standard Franklin lightning sensor with a precision-wound 500 kHz detection antenna. The sensor features a hardware-embedded lightning detection algorithm that analyses incoming electromagnetic signatures and differentiates genuine lightning events from man-made electromagnetic disturbances.

## 3.2 EMI Rejection

The system is designed for deployment in environments with significant electromagnetic interference. The sensor's built-in disturber rejection algorithm identifies and filters interference from common sources including:

Electric arc and induction furnaces

Variable-frequency drives (VFDs) and large motor starters

Overhead crane motors and slip-ring arcing

High-current bus bars and switchgear

Welding equipment

Switch-mode power supplies

High-intensity discharge (HID) lighting

The EMI rejection parameters are fully configurable to suit the specific noise profile of each installation site. On-site calibration is performed during commissioning to optimise detection sensitivity while minimising false positive rates.

## 3.3 Configurable Filter Settings

For sites with high ambient electromagnetic noise, the system is deployed with conservative filter settings:

Elevated noise floor to reject persistent broadband interference

Higher watchdog threshold for transient spike rejection

Aggressive spike rejection filtering

Multi-event validation before alert issuance

Outdoor analogue front-end mode (reduced gain)

These settings are optimised during on-site commissioning and can be remotely adjusted as required. The target false positive rate is < 1 false event per day under typical conditions.

## 3.4 Antenna Calibration

Each unit undergoes antenna calibration during commissioning to ensure optimal performance. The antenna resonance is verified to be within 3.5% of the 500 kHz target frequency (482.5 – 517.5 kHz). Calibration is performed using a proprietary software utility and the results are stored in the system configuration.

# 4. Data Output and Communication

## 4.1 Cloud Data Publishing

| Parameter | Specification |
| --- | --- |
| Protocol | HTTPS POST (JSON payload) |
| Encryption | TLS 1.2+ (end-to-end) |
| Authentication | API key (per-station) |
| Dashboard | Real-time web-based visualisation |
| Offline Handling | Automatic local buffering with retry and sync on reconnect |

Published data fields include:

Lightning distance (km)

Lightning energy (relative)

System heartbeat and health status

Additional sensor fields supported (temperature, humidity, pressure, wind speed, rainfall, battery voltage)

## 4.2 Local Data Logging

| Parameter | Specification |
| --- | --- |
| Format | CSV (comma-separated values) |
| File Rotation | Daily (midnight UTC) |
| Storage Capacity | Years of continuous logging |
| Data Fields | Timestamp (UTC), event type, distance (km), energy, system parameters |
| Compatibility | Direct import to Excel, SCADA, LoggerNet, and data analysis tools |

## 4.3 Data Access

Real-time: Cloud dashboard via web browser

Historical: Local CSV download via secure network connection

Integration: Compatible with existing SCADA and data management systems via cloud API or local file export

# 5. Alert and Notification Features

## 5.1 Proximity Alerts

The system generates automatic alerts when lightning is detected within a configurable proximity threshold.

| Parameter | Specification |
| --- | --- |
| Default Alert Distance | 10 km (configurable) |
| Alert Cooldown Period | 60 minutes (configurable) |
| Alert Channels | SMS, WhatsApp, Email |
| Multiple Recipients | Yes (configurable per channel) |
| Alert Content | Distance to storm, timestamp, station identifier |

## 5.2 Weekly Summary Reports

Automated weekly lightning activity reports are generated and distributed via email. Reports include:

Reporting period (7-day summary)

Total lightning events detected

Closest lightning approach distance

Average and maximum lightning energy

System uptime and health summary

| Parameter | Specification |
| --- | --- |
| Report Schedule | Configurable day and time (default: Monday 07:00) |
| Report Format | PDF (A4) |
| Delivery | Email with PDF attachment |

# 6. Power System Specifications

## 6.1 Power Supply

| Parameter | Specification |
| --- | --- |
| Primary Power Source | Solar panel (6–24 V DC input) |
| Solar Charge Controller | MPPT (Maximum Power Point Tracking) |
| Battery Type | 3.7 V Lithium-ion |
| Battery Configuration | 3 cells parallel (3P) |
| Battery Capacity | 9,000 – 10,500 mAh (33–39 Wh) |
| Charge Protection | Over-charge, over-discharge, over-temperature, over-current |
| Output Voltage | 5 V regulated |
| Output Current | 3 A maximum |

## 6.2 Power Consumption

| Parameter | Specification |
| --- | --- |
| Typical Power (listening) | ~1.4 W |
| Peak Power (wireless transmit) | ~2.2 W |
| Daily Energy Budget | ~18–36 Wh (usage dependent) |

## 6.3 Battery Autonomy (No Solar)

| Condition | Runtime |
| --- | --- |
| Typical operation | 25+ hours |
| Power-optimised mode | 46+ hours |

## 6.4 Solar Requirements

Minimum recommended panel: 5 W (6–24 V output). The system is energy-positive with 5 W of available solar input and 4–6 peak sun hours per day. The system can integrate with existing solar panel infrastructure or operate from a dedicated panel.

# 7. Environmental Ratings

## 7.1 Operating Conditions

| Parameter | Specification |
| --- | --- |
| Operating Temperature | −20 °C to +60 °C |
| Storage Temperature | −30 °C to +70 °C |
| Humidity | 0–100% RH (non-condensing) |
| Ingress Protection | IP65 minimum (IP67 available) |
| UV Resistance | UV-stabilised enclosure material |
| Wind Survival | 150 km/h (with mast mounting) |
| Altitude | 0 – 5,000 m ASL |

## 7.2 Enclosure

| Parameter | Specification |
| --- | --- |
| Material | ABS or polycarbonate (non-metallic) |
| RF Transparency | Optimised for 500 kHz reception |
| Cable Entry | IP68-rated cable glands (bottom entry) |
| Mounting | Rear-mount plate with U-bolt or pole clamp |
| Seal Type | Gasket seal (IP65 / IP67) |

## 7.3 Lightning Survivability

The system should be mounted below an existing lightning protection system (lightning rod / air terminal). External transient voltage suppression is recommended on the solar input cable. The system includes internal input protection circuitry.

# 8. Mechanical Specifications

## 8.1 Dimensions and Weight

| Parameter | Specification |
| --- | --- |
| Enclosure Dimensions (typical) | 150 × 150 × 90 mm (W × H × D) |
| Mounting Plate | Aluminium, corrosion-resistant finish |
| Mounting Hardware | 316 stainless steel U-bolts |
| Cable Glands | PG9 / M16, IP68 rated |
| Mast Compatibility | 30–50 mm diameter (adjustable) |
| Approximate System Weight | < 1.0 kg (including batteries) |

## 8.2 Mounting Requirements

Non-metallic enclosure positioned with antenna facing away from mast and away from major EMI sources

Minimum 50 cm separation from other electronic equipment

Minimum 30 cm clearance from large metal surfaces

Bottom cable entry for water run-off protection

Elevated mast position recommended for optimal reception

# 9. Installation Requirements

## 9.1 Site Requirements

Weather station mast or suitable mounting pole (30–50 mm diameter)

Solar panel (6–24 V output, 5 W minimum) or existing solar infrastructure

2.4 GHz Wi-Fi network coverage at installation location

Clear line of sight to sky (no overhead metallic structures directly above the sensor)

## 9.2 Commissioning Services

Professional installation and commissioning services include:

Physical installation and mounting

Antenna calibration and frequency verification

EMI noise profiling and filter optimisation

Cloud platform configuration and verification

Alert recipient configuration and test notifications

Commissioning report and handover documentation

## 9.3 Network Requirements

2.4 GHz Wi-Fi (802.11 b/g/n) with internet access

HTTPS outbound access (port 443) to cloud platform

NTP access (port 123) for time synchronisation

SMTP access (port 587) for email report delivery (if enabled)

# 10. Maintenance Schedule

| Frequency | Activity |
| --- | --- |
| Monthly | Verify system operation via cloud dashboard Review alert history and data integrity |
| Quarterly | Inspect enclosure seal and mounting hardware Clean solar panel and cable connections Review and archive data files |
| Annually | Replace lithium-ion batteries Replace desiccant packs Inspect internal components and cabling Re-calibrate antenna if required Software update (if available) |
| Bi-annually | Replace storage media (preventative) Full system functional verification |

# 11. Performance Comparison

The system offers comparable detection performance to commercial lightning detection systems at a significantly reduced cost and power footprint:

| Feature | This System | Commercial Systems |
| --- | --- | --- |
| Detection Range | 40 km | 40–50 km |
| Distance Accuracy | +/- 4 km | +/- 4 km |
| Direction Finding | No | Yes (some models) |
| Detection Types | CG + IC | CG + IC |
| EMI Rejection | Yes (configurable) | Yes |
| Power Consumption | < 2.5 W | 5–15 W |
| Solar Compatible | Yes (standard) | Limited |
| Cloud Dashboard | Yes (included) | Varies (often extra cost) |
| SMS / WhatsApp Alerts | Yes (included) | Rarely included |
| Weekly PDF Reports | Yes (included) | Rarely included |
| Offline Buffering | Yes (automatic) | Varies |
| Maintenance | Low | Moderate–High |

# 12. Limitations and Disclaimers

## 12.1 System Limitations

The system estimates distance to the storm front, not to individual lightning strikes.

No direction or bearing information is provided (distance only).

Detection sensitivity may be lower than high-end commercial systems with large external antenna arrays.

Distance estimation accuracy is +/- 4 km under optimal conditions.

Performance may be reduced in extremely high EMI environments despite aggressive filtering. Site assessment is recommended prior to deployment.

Battery runtime is reduced at temperatures below 0 °C.

Requires 2.4 GHz Wi-Fi coverage for cloud publishing and alerts. Local logging continues without connectivity.

## 12.2 Certification and Compliance

This system is NOT a certified meteorological instrument.

Data is indicative and intended for safety awareness, operational decision support, and general weather monitoring.

Data should not be used as the sole basis for official weather reporting without independent validation.

The system is designed as a complement to, not replacement for, certified lightning protection systems and safety procedures.

All lightning safety protocols and evacuation procedures should remain in effect regardless of system status.

# 13. Ordering and Support

## 13.1 Standard Package Includes

Lightning detection unit (fully assembled and tested)

Weatherproof IP65+ enclosure with mounting hardware

Lithium-ion battery pack (pre-installed)

Stainless steel mast mounting kit

Cable glands and power cable

Desiccant packs

Cloud platform account and configuration

Professional installation and commissioning

Commissioning report and system documentation

12-month support

## 13.2 Optional Add-Ons

Dedicated solar panel (6 V / 5 W or 12 V / 10 W)

Extended battery pack for increased autonomy

Cellular connectivity module (for sites without Wi-Fi)

GPS timing module (for sites without internet / NTP)

Hardware real-time clock (RTC) for power-loss time retention

Integration with Campbell Scientific or other datalogger systems

Extended support and maintenance agreements

____________________________________________________________

This document is provided for reference purposes only.
Specifications are subject to change without notice.
Contact your representative for the latest information.